Preliminary information for the planning company

The following text for invitations to tender is intended to assist you in the preparation of service specifications.

We ask you to clearly identify the device that is suitable for the project and to delete the device types (article numbers) that have not been selected.

Portable hydrant tester for measuring pressure, flow rate, temperature and turbidity1) (battery operated incl. data logger) to check the quantity of extinguishing water and to perform flushing (according to drinking water guidelines)

Magnetic inductive flowmeter with pulsed DC field, piezo resistive pressure transmitter and platinum resistance sensor

APPROVALS

CE marking acc. to. directive:

- 2014/30/EU (EMV)

- 2014/53/EU (RED)

condition of use

Media temperature range: 	+1 °C to +40 °C (+39 °F to +122 °F)

Pressure limit: 	PN 16 (232 psi)

Measuring accuracy 
Flow:	±0,5 % of the measured value
Pressure:	±0,25 % of the measuring range full scale value
Temperature:	±1,0 % of the measured value

Process connection:	turnable and exchangeable Storz (threaded – alternative process 
 	connections on request

features

- no moving parts

- free flow (no additional pressure losses)

- including pressure sensor, optional temperature and turbidity1)

- including data memory for 2 000 000 measured values

- including 5 point calibration certificate

- data transmission via Bluetooth

- 5 inch LCD display, illuminated display (240 x 128 pixel)

- great stability

- measuring accuracy: ±0.5 % of the measured value

- operating pressure Pe: max. 16 bar

- temperature of medium: +1 to +40 °C

- protection class IP54

Free first recalibration at the factory after 2 years incl. calibration certificate. Calibration stands are equipped with reference instruments according to EN 17025.
1) Preparation for separate turbidity measurement HTL TE/TU

Measung ranges

| Flow rate |  | Description | Model |
| --- | --- | --- | --- |
| (l/min.) | (m³/h) |  |  |
| 0 … 905 | 0 … 54,3 | diameter DN 40 / 1½“, Storz C rotatable | HTL040 |
| 0 … 1 413 | 0 … 84,8 | diameter DN 50 / 2“, Storz C rotatable | HTL050 |
| 0 … 2 390 | 0 … 143,4 | diameter DN 65 / 2½“, Storz B rotatable | HTL0650 |
| 0 … 3 619 | 0 … 217,2 | diameter DN 80 / 3“, Storz B rotatable | HTL080 |
| 0 … 5 655 | 0 … 339,3 | diameter DN 100 / 4“, Storz A rotatable | HTL100 |
| 0 …12 723 | 0 … 763,4 | diameter DN 150 / 6“, Storz 150 rotatable | HTL150 |

Optional to pressure and flow measurement:

TE	temperature measurement for HTL040 to HTL150

TE/TU	temperature- and turbidity measurment (preparation) for HTL050 to HTL100

Manufacturer: 	MECON GmbH

Type: 	mag-flux HTL

APP wasserkarte.info (www.wasserkarte.info)

- data transfer via Bluetooth from the hydrant tester to the mobile device via app (Android)

- start measurements directly via the app and record them directly

- reading out the measurement data and configuration of the devices

- archive system supported by a data base

- extensive functionalities for digital hydrant management

pressure reducer (flush box) – for the safe flushing of hydrants

| Flow rate |  | Description | Model |
| --- | --- | --- | --- |
| (l/min.) | (m³/h) |  |  |
| 0 … 3 619 | 0 … 216 | pressure reducer Storz C (incl. hose coupling C to B) | HTLDV050 |
| 0 … 3 619 | 0 … 216 | pressure reducer Storz B | HTLDV080 |
| 0 … 7 238 | 0 … 432 | pressure reducer Storz A (consisting of 2 x pressure reducer Storz B, 2 x hose coupling with each 5 m, 1 x fork) | HTLDV100 |

- material from stainless steel

- stable standing, even at high flow rates

- max. to 216 m³/h (3 600 l/min.) - Storz B

- no pressure loss

- no recoil forces

- no washout on unpaved ground

- no danger for the environment

- clean and space saving

Regulation valve

- Regulation valve in brass

- 2 Storz connections with fixed coupling in aluminium

| Description | Model |
| --- | --- |
| regulation valve connection Storz C (DN 40/50) | HTLAR050 |
| regulation valve connection Storz B (DN 65/80) | HTLAR080 |
| regulation valve connection Storz A (DN 100) | HTLAR100 |

Transpor case

Easy transport of the equipment and accessories

- dust- and waterproof acc. MIL C-4150J

- resistant to UV, solvents, corrosion and fungi

- ultra high strength polypropylene copolymer resin material

- high-strength transport case for the types HTL040, 050 and 080 incl. push handle and two transport wheels

- safe storage of the measuring device, power supply unit and control valve

- incl. PE foam inlay for optimal protection

| Description | Model |
| --- | --- |
| Transport case (for HTL040, 050, 065 and 080) | HTLTC |

fire hose

Fire hose B-75; DIN 14811, white, with Storz B coupling; wire / clamp binding

| Description | Model |
| --- | --- |
| length: 0,5 m | 10970 |
| length: 1,7 m | 10971 |
| length: 3,0 m | 10972 |
| length: 5,0 m | 10973 |
| length: 10,0 m | 10975 |
| length: 15,0 m | 10974 |

Contact: Michael Juech, +49 (0)22 37 60006-14, m.juech@mecon.de